## Analysis
ID_No | Date | State | PMU | Primary Voltage | Bay | Object | Root Cause | Cause | Defect/Trip Description | Report
Data set 1
20169303 | 2009-10-26 | Perak | BMRH | 132 | TX_4 |  | TCBL06 | 1000-UNKNOWN | BMRH 410-Bph SA need to replace | 29.10.2009 11:09:48 Noreen Natasha Binti Mohd Lod (74567)¦WHAT- Tandelta-failed for bottom stack of SA (low reading compare to Rph¦<(>&<)> Yph)¦WHERE - BMRH bay 410¦WHO - CMU IPOH¦WHO REPORT - CMU AM IPOH¦WHO ATTEND - CMU IPOH <(>&<)> TEAM D S/S¦WHY DID THE FAULT OCCURED - Semasa kerja senggaraan CMU- tandelta¦HOW THE FAULT RESOLVED - Perlu menukar SA
20172211 | 2009-10-26 | Perak | BMRH | 132 | TX_4 |  | TSUBS1 | 1003-EXCEED TEST LIMIT | BMRH 410-Bph SA need to replace | 08.12.2009 11:44:58 Noreen Natasha Binti Mohd Lod (74567)¦WHAT- Tandelta-failed for bottom stack of SA (low reading compare to Rph¦<(>&<)> Yph)¦WHERE - BMRH bay 410¦WHO - CMU IPOH¦WHO REPORT - CMU AM IPOH¦WHO ATTEND - CMU IPOH <(>&<)> TEAM D S/S¦WHY DID THE FAULT OCCURED - Semasa kerja senggaraan CMU- tandelta¦HOW THE FAULT RESOLVED - Perlu menukar SA
T10171 | 2010-01-20 | Perak | BMRH | 132 | TX_4 |  | Subsidiary System | TNBD | Tripping caused by failure of 33/0.11 kV VT at 4TO LV CB. CO2 system operated and discharged in the 33kV switchgear room. Contractor already called to repair on FFD (near to discharge nozzle) | There was an actual system fault due to LV VT (ETAH) explosion at 4T0. Transformer tripped on Tx Diff to isolate the fault.
Data set 2
30051449 | 2007-03-16 | Perak | BSRI | 132 | TX_2 |  | GENERAL | 1001-PM SCHEDULED WORK | BSRI-TX 2 THIGHTEN TB & BATT.MTCE
30051764 | 2007-03-23 | Perak | BSRI | 132 | TX_2 |  | GENERAL | 1000-NOT KNOWN | BSRI-T2 AVR INVESTIGATION
20207203 | 2011-02-21 | Perak | BSRI | 132 | TX_2 | 1001-CONTACT MOVING CONTACT | TSUBS1 | 1005-HOT SPOT | BSRI 210-Isolator contact 214 hotspot | 02.03.2011 17:01:48 Noreen Natasha Binti Mohd Lod (74567)¦WHAT- Hotspot found on isolator contact 214 Bph=60dc,Rph=50.4dc¦WHERE - BSRI 210¦WHO - CMU AM IPOH¦WHO REPORT - CMU AM IPOH¦WHO ATTEND - CMU AM IPOH¦WHY DID THE FAULT OCCURED - Semasa kerja senggaraan CMU- thermovision.¦Kemungkinan loose contact pada bolt <(>&<)> nut, karat¦HOW THE FAULT RESOLVED - perlu mengambil shutdown untuk membaikpulih¦hotspot-cuci <(>&<)> tighten semula bolt <(>&<)> nut pada clamp
20232701 | 2012-01-17 | Perak | BSRI | 132 | TX_2 | 1011-CONSERVATOR/MAIN TANK | TSUBS1 | 1004-LEAKS | BSRI T2 132/11 KV 30 MVA | 17.01.2012 15:20:13 Noor Helmi Bin Md Rasid (74617)¦BSRI T2 Kebocoran Minyak Pada Inspection Cover Main Tank.Cadangan Henti¦Tugas <(>&<)> Baiki Kebocoran.
20250932 | 2012-04-20 | Perak | BSRI | 132 | TX_2 |  | TDEFECEQ | 1003-DEGRADING | BSRI T2-Oil resampling requested by HQ | 13.08.2012 11:08:11 Noreen Natasha Binti Mohd Lod (74567)¦Resampling oil to sent to TNBR for DGA test after HQ requested to do¦after all tx that has done reclaimation
20250929 | 2012-04-27 | Perak | BSRI | 132 | TX_2 |  | TDEFECEQ | 1003-DEGRADING | BSRI T2-Test BDV low on site | 13.08.2012 10:53:40 Noreen Natasha Binti Mohd Lod (74567)¦As per Pejabat DVPT on intruction to test low BDV result on XGT,SGT,TX¦<(>&<)> ETX on site.¦13.08.2012 11:40:51 Noreen Natasha Binti Mohd Lod (74567)¦To test portable DGA requested by HQ for tx after done oil reclaimation
20249326 | 2012-07-24 | Perak | BSRI | 132 | TX_2 | 1009-OLTC MOTOR DRIVE AND MECHANISM | TSUBS1 | 1004-LEAKS | BSRI T2 132/11 KV 30 MVA | 24.07.2012 14:46:26 Noor Helmi Bin Md Rasid (74617)¦KEBOCORAN MINYAK PADA MAIN INSPECTION COVER OLTC.TINDAKAN HENTI TUGAS¦<(>&<)> BAIKI KEBOCORAN.
20272393 | 2013-06-04 | Perak | BSRI | 132 | TX_2 | 1016-CABLE BOX | TSUBS1 | 1004-LEAKS | BSRI T2 132/11 KV 30 MVA | 04.06.2013 10:04:09 Noor Helmi Bin Md Rasid (74617)¦Kebocoran Minyak Pada LV Cable Box <(>&<)> Radiator.Tindakan Henti Tugas¦Dan Baiki Kebocoran
20276260 | 2013-07-16 | Perak | BSRI | 132 | TX_2 | 1004-INSULATING MEDIUM VACUUM | TSUBS3 | 1001-OTHERS | BSRI-TX 2 trip on differential relay | 18.07.2013 10:25:52 Rosman Bin Abdullah (72974)¦WHERE - BSRI¦WHO - ROSMAN¦WHO REPORT - ROSMAN¦WHO ATTEND - TEAM B¦WHY DID THE FAULT OCCURED - unknown¦HOW THE FAULT RESOLVED - cuci sarang burung
20276203 | 2013-07-16 | Perak | BSRI | 132 | TX_2 | 1006-RELAY/IED OTHERS COMPONENT | TPROT05 | 1000-UNKNOWN | BSRI: Tx 2 Tripping
T13328 | 2013-07-16 | Perak | BSRI | 132 | TX_2 |  | Subsidiary System | TNBD | Tripping due to 11kV busbar fault (CB 32 exploded) | An actual system fault in CB compartment for CB32. The flashover was on the CB truck. CB34 was on open condition during the incident.
Defect Details
Tripping details

## Summary
| Trip |  |  |  |  | Defect
Functional Location | TripID | TripDescription | Report | Primary Cause | Root Cause | DefectID | DefectDescription | Object | Root Cause | Cause | Report
Perak/BMRH/132/TX_4 | T10171 | Tripping caused by failure of 33/0.11 kV VT at 4TO LV CB. CO2 system operated and discharged in the 33kV switchgear room. Contractor already called to repair on FFD (near to discharge nozzle) | There was an actual system fault due to LV VT (ETAH) explosion at 4T0. Transformer tripped on Tx Diff to isolate the fault. | Subsidiary System | TNBD | 20172211 | BMRH 410-Bph SA need to replace | 0 | TSUBS1 | 1003-EXCEED TEST LIMIT | 08.12.2009 11:44:58 Noreen Natasha Binti Mohd Lod (74567)¦WHAT- Tandelta-failed for bottom stack of SA (low reading compare to Rph¦<(>&<)> Yph)¦WHERE - BMRH bay 410¦WHO - CMU IPOH¦WHO REPORT - CMU AM IPOH¦WHO ATTEND - CMU IPOH <(>&<)> TEAM D S/S¦WHY DID THE FAULT OCCURED - Semasa kerja senggaraan CMU- tandelta¦HOW THE FAULT RESOLVED - Perlu menukar SA
[6 empty] | 20169303 | BMRH 410-Bph SA need to replace | 0 | TCBL06 | 1000-UNKNOWN | 29.10.2009 11:09:48 Noreen Natasha Binti Mohd Lod (74567)¦WHAT- Tandelta-failed for bottom stack of SA (low reading compare to Rph¦<(>&<)> Yph)¦WHERE - BMRH bay 410¦WHO - CMU IPOH¦WHO REPORT - CMU AM IPOH¦WHO ATTEND - CMU IPOH <(>&<)> TEAM D S/S¦WHY DID THE FAULT OCCURED - Semasa kerja senggaraan CMU- tandelta¦HOW THE FAULT RESOLVED - Perlu menukar SA
Perak/BSRI/132/TX_2 | T13328 | Tripping due to 11kV busbar fault (CB 32 exploded) | An actual system fault in CB compartment for CB32. The flashover was on the CB truck. CB34 was on open condition during the incident. | Subsidiary System | TNBD | 20276203 | BSRI: Tx 2 Tripping | 1006-RELAY/IED OTHERS COMPONENT | TPROT05 | 1000-UNKNOWN
[6 empty] | 20276260 | BSRI-TX 2 trip on differential relay | 1004-INSULATING MEDIUM VACUUM | TSUBS3 | 1001-OTHERS | 18.07.2013 10:25:52 Rosman Bin Abdullah (72974)¦WHERE - BSRI¦WHO - ROSMAN¦WHO REPORT - ROSMAN¦WHO ATTEND - TEAM B¦WHY DID THE FAULT OCCURED - unknown¦HOW THE FAULT RESOLVED - cuci sarang burung
[6 empty] | 20272393 | BSRI T2 132/11 KV 30 MVA | 1016-CABLE BOX | TSUBS1 | 1004-LEAKS | 04.06.2013 10:04:09 Noor Helmi Bin Md Rasid (74617)¦Kebocoran Minyak Pada LV Cable Box <(>&<)> Radiator.Tindakan Henti Tugas¦Dan Baiki Kebocoran
[6 empty] | 20249326 | BSRI T2 132/11 KV 30 MVA | 1009-OLTC MOTOR DRIVE AND MECHANISM | TSUBS1 | 1004-LEAKS | 24.07.2012 14:46:26 Noor Helmi Bin Md Rasid (74617)¦KEBOCORAN MINYAK PADA MAIN INSPECTION COVER OLTC.TINDAKAN HENTI TUGAS¦<(>&<)> BAIKI KEBOCORAN.
[6 empty] | 20250929 | BSRI T2-Test BDV low on site | 0 | TDEFECEQ | 1003-DEGRADING | 13.08.2012 10:53:40 Noreen Natasha Binti Mohd Lod (74567)¦As per Pejabat DVPT on intruction to test low BDV result on XGT,SGT,TX¦<(>&<)> ETX on site.¦13.08.2012 11:40:51 Noreen Natasha Binti Mohd Lod (74567)¦To test portable DGA requested by HQ for tx after done oil reclaimation
[6 empty] | 20250932 | BSRI T2-Oil resampling requested by HQ | 0 | TDEFECEQ | 1003-DEGRADING | 13.08.2012 11:08:11 Noreen Natasha Binti Mohd Lod (74567)¦Resampling oil to sent to TNBR for DGA test after HQ requested to do¦after all tx that has done reclaimation
[6 empty] | 20232701 | BSRI T2 132/11 KV 30 MVA | 1011-CONSERVATOR/MAIN TANK | TSUBS1 | 1004-LEAKS | 17.01.2012 15:20:13 Noor Helmi Bin Md Rasid (74617)¦BSRI T2 Kebocoran Minyak Pada Inspection Cover Main Tank.Cadangan Henti¦Tugas <(>&<)> Baiki Kebocoran.
[6 empty] | 20207203 | BSRI 210-Isolator contact 214 hotspot | 1001-CONTACT MOVING CONTACT | TSUBS1 | 1005-HOT SPOT | 02.03.2011 17:01:48 Noreen Natasha Binti Mohd Lod (74567)¦WHAT- Hotspot found on isolator contact 214 Bph=60dc,Rph=50.4dc¦WHERE - BSRI 210¦WHO - CMU AM IPOH¦WHO REPORT - CMU AM IPOH¦WHO ATTEND - CMU AM IPOH¦WHY DID THE FAULT OCCURED - Semasa kerja senggaraan CMU- thermovision.¦Kemungkinan loose contact pada bolt <(>&<)> nut, karat¦HOW THE FAULT RESOLVED - perlu mengambil shutdown untuk membaikpulih¦hotspot-cuci <(>&<)> tighten semula bolt <(>&<)> nut pada clamp
[6 empty] | 30051764 | BSRI-T2 AVR INVESTIGATION | 0 | GENERAL | 1000-NOT KNOWN
[6 empty] | 30051449 | BSRI-TX 2 THIGHTEN TB & BATT.MTCE | 0 | GENERAL | 1001-PM SCHEDULED WORK

## Sheet1
Business Objective
To Classify root causes of the transformer trip and also identify the strong parameters which are associated with trip